SECTION 233433

AIR CURTAINS

Important Note: This document contains hidden text appearing in magenta. The final document should not display the hidden text. To remove hidden text, click the “File” tab or “Office” icon on the top-left corner, select “Options,” select “Display,” and uncheck the box marked “Hidden Text.”

** NOTE TO SPECIFIER ** Mars Air Systems, LLC; for Mars Low Profile 2 Series air curtains for environmental control, insect control and temperature control.

.

This section is based on products manufactured by Mars Air Systems, LLC, which is located at:

14716 South Broadway St.

Gardena, CA 90248

Tel: (310) 532-1555

Tel: (800) 421-1266

Fax: (310) 324-3030

Email: info@marsair.com

Web: www.marsair.com

[click Here] for additional information.

Mars Air Systems, LLC. manufactures energy savings air curtains that make buildings more functional for work, dining, shopping and play. From manufacturing facilities, warehouses and convention centers to buy-in-bulk retail stores, restaurants and sports complexes, Mars Air Curtains can be installed over any operational door or pass-thru window. Mars Air Curtains will protect a building's inside environment from windborne dust, dirt, fumes, flying insects and extreme outside temperature conditions. Mars offers a complete line of air curtains available with a variety of heat options, color and mounting options, and a multitude of accessories to customize your air curtain for any application setting. Heating options include electric, and steam hot water coils. Not only will Mars Air Curtains improve the inside sanitation levels of your facility, but it will also reduce the operational energy costs necessary to heat and cool it.

Typical installations include retail entrances, pedestrian and vehicular openings, and large loading dock doors. Air curtains help reduce heating and cooling costs while expediting the flow of traffic from one work area to another or in and out of a building. At the same time, air curtains repel gusts of wind and minimize the entrance of windborne dust, fumes, pollutants, and flying insects.

Mars Air Curtain products meet the requirements of all North American and European Union Codes and Standards. For a complete selection guide and assistance with your air curtain configuration please visit www.marsair.com. For additional information and assistance call Mars Air Systems at 800-421-1266 or 310-532-1555.

- GENERAL

  - SECTION INCLUDES

** NOTE TO SPECIFIER **  Delete items below not required for project.

    - Air curtains for pedestrian entrances.

    - Air curtains for vehicular entrances.

  - RELATED SECTIONS

** NOTE TO SPECIFIER **  Delete any sections below not relevant to this project; add others as required.

    - Section 05500 - Metal Fabrications: Concealed steel support members.

    - Section 06100 - Rough Carpentry.

    - Section 05410 - Load-Bearing Metal Studs.

    - Section 07900 - Joint Sealers.

    - Section 08110 - Steel Doors and Frames.

    - Section 08330 - Overhead Coiling Doors.

    - Section 15145 - Plumbing Piping:

    - Section 15182 - Hydronic Piping:  Hot water heating piping to units.

    - Section 15184 - Steam and Condensate Piping:  Steam heating piping to units.

    - Section 16150 (20 05 00) - Equipment Wiring:  Connections to building power distribution.

  - REFERENCES

** NOTE TO SPECIFIER **  Delete references from the list below that are not actually required by the text of the edited section.

    - ASTM A240 / A240M -10 – Standard Specification for Chromium and Chromium-Nickel Stainless Steel Plate, Sheet, and Strip for Pressure Vessels and for General Applications.

    - ASTM A591 / A591M -98 – Standard Specification for Steel Sheet, Electrolytic Zinc-Coated, for Light Coating Weight (Mass) Application (Withdrawn in 2005, replaced by A879/A879M).

    - ASTM A879 / A879M -06 – Standard Specification for Steel Sheet, Zinc Coated by the Electrolytic Process for Application Requiring Designation of the Coating Mass on Each Surface.

    - ASTM A653 / A653M -09a – Standard Specification for Steel Sheet, Zinc Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process.

    - UL 507 – Standard for Safety Electric Fans – UL Listed for US and Canada.

    - UL 507 – UL Standard for Safety Electric Fans – Intertek Testing Services Listed for US and Canada.

    - UL 2021 – UL Standard for Fixed and Location-Dedicated Electric Room Heaters – Listed for US and Canada.

    - UL 2021 – Standard for Fixed and Location-Dedicated Electric Room Heaters – Intertek Testing Services Listed for US and Canada.

    - ARI 410-2001 – Standard for Forced-Circulation Air-cooling and Air-Heating Coils.

** NOTE TO SPECIFIER **  The following paragraph is an optional standard and must be specified if needed.

    - CRN – Canadian Registration Number Coil.

    - NSF 37 – Air Curtains for entranceways in food and food service establishments – ETL Sanitation

    - NEC – National Electric Code.

  - SUBMITTALS

    - Submit under provisions of Section 01300.

    - Product Data:  Manufacturer's data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation methods.

    - Shop Drawings: Include plans, elevations, sections, and details, indicating dimensions, tolerances, materials, fasteners, hardware, finish, piping, electrical wiring diagrams, options, and accessories.

** NOTE TO SPECIFIER **  Delete selection samples if colors have already been selected.

    - Selection Samples:  For each finish product specified, two complete sets of color chips representing manufacturer's full range of available colors and patterns.

    - Verification Samples:  For each finish product specified, two samples, minimum size 6.25 inches (160 mm) square, represent actual product, color, and patterns.

    - Manufacturer's Certificates: Certify products meet or exceed specified requirements.

    - Operation and Maintenance Manual:  Submit manufacturer's operation and maintenance manual, including operation, maintenance, adjustment, and cleaning instructions, trouble shooting guide, parts list, and electrical wiring diagrams.

  - QUALITY ASSURANCE

    - Manufacturer Qualifications: Minimum ten years documented experience producing the products specified in this Section.

    - Installer Qualifications: Minimum five years documented experience installing products specified in this Section.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer's unopened packaging until ready for installation.

    - Store in a dry, heated storage area until installation of products.

    - Protect materials and finish from damage during handling and installation.

  - SEQUENCING

    - Ensure that locating templates and other information required for installation of products of this section are furnished to affected trades in time to prevent interruption of construction progress.

    - Coordinate the installation of wiring and control switches for air curtains with the openings and the hardware provided for such openings.

    - Install after doors, walls, ceilings and other adjacent surfaces are finished and painted.

  - WARRANTY

** NOTE TO SPECIFIER **  Select the applicable warranty from the following paragraphs as required for the unit(s) specified and delete the one not required.

    - Standard five year limited parts warranty for unheated units against defects in workmanship and material.

    - Standard eighteen-month limited parts warranty for heated units against defects in workmanship and materials.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer: Mars Air Systems, LLC; 14716 South Broadway St., Gardena, CA 90248. Tel: (310) 532-1555 or (800) 421-1266.  Fax: (310) 324-3030.  Email: info@marsair.com.  Web: www.marsair.com.

** NOTE TO SPECIFIER **  Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions:  Not permitted.

    - Requests for substitutions will be considered in accordance with provisions of Section 01600.

** NOTE TO SPECIFIER ** Low Profile Series air curtains are available in two types: Environmental and Flying Insect (ETL Sanitation) Control.  They are available for openings 25 inches to 144 inches wide and heights up to 8 feet for environmental separation and temperature control applications and heights up to 7 feet for flying insect control applications (ETL Sanitation). Countertop and/or concessions stand installation require intake filters. Low Profile Series air curtains for temperature control applications are typically effective to resist wind loads up to 9 mph. Note that velocities specified for each unit are based on a 60 Hz power source.

Select the type and sizes required and delete those not required. Indicate the door/opening height for each air curtain on the Drawings or on the Schedule at the end of this Section. If more than one type and/or size is required, indicate the location of each on the Drawings or on the Schedule at the end of this Section.

  - AIR CURTAIN ASSEMBLIES

    - Motor and Fan Assembly: Design for easy removal, assembly, repair and maintenance.

      - Motor: Totally enclosed air over (TEAO) cooled motor with sealed lifetime pre-lubricated ball bearings, motor starter and thermal overload protection.

** NOTE TO SPECIFIER ** Select one of the following two paragraphs and delete the ones not required.

        - LPN2 Units: Wired for single speed operation.

        - LPV2 Units: Wired for variable speed operation.

** NOTE TO SPECIFIER ** Select one of the following two paragraphs and delete the one not required. Note that Electrical Characteristics below do not include electric heater requirements. Note that all motors listed are based on 60 Hz service. For units wider than 84 inches, refer to submittal for total amps. For other voltages, contact manufacturer.

        - Electrical Characteristics: 115V AC, single phase; 2.4 Amp (units up to 48 inches wide) or 2.6 Amp (units 60 to 72 inches wide) full load per motor/fan.

        - Electrical Characteristics: 208/230V AC, single phase; 1.2 Amp (units up to 48 inches wide) 1.4 Amp (units 60 to 70 inches wide) full load per motor/fan.

      - Fans:  Tangential type, double width, directly driven by an electric motor.

      - Provide resilient isolation dampening mountings between motor frame and housing.

      - Factory balanced blower wheel assembly statically and dynamically.

    - Housing: Self-contained one-piece type for units up to 72 inches in length with sufficient strength for mounting from pre-punched mounting holes at both ends to ceiling without intermediate support. Units longer than 72” are two units tandem mounted next to each other.

      - Size:

** NOTE TO SPECIFIER ** Select one of the following paragraphs and delete the ones not required. Heated units are mounted inside only; coordinate with heating paragraphs if required.

        - Unheated: 7-7/8 inches deep by 8 inches high (including discharge nozzle) by width of unit.

        - Electric Heated: 10-3/4 inches deep by 8 inches high (including discharge nozzle) by width of unit.

        - Hot Water/Steam Heated: Depth 10-3/4 inches by 8 inches high including discharge nozzle by width of unit plus 10 inches for manifolds.

      - Mounting:

** NOTE TO SPECIFIER ** Select one of the following paragraphs and delete the ones not required. Heated units are mounted inside only; coordinate with heating paragraphs if required.

        - Unheated Inside Mount.

        - Heated Inside Mount.

        - Unheated Outside Mount.

        - Mount Location Indicated.

      - Material:

** NOTE TO SPECIFIER ** Select one of the following two paragraphs and delete the one not required.

        - Provide 18 and 20 gauge electro or hot dipped galvanized steel sheet housing conforming to ASTM A 591 and/or ASTM A 653.

        - Provide type 304 stainless steel housing with brushed finish. ASTM A 240/A 240M.

      - Air Inlet Grille and/or Filters: Provide air inlet grille and/or filters specified.

      - Discharge: Provide integral discharge nozzle specified.

** NOTE TO SPECIFIER ** Select following paragraph for sheet steel housings only. Delete entirely for stainless steel housing. Select color required for steel housing and delete the ones not required. Obsidian Black is standard.

      - Finish and Color: Provide with, no VOC, corrosion resistant polyurethane powder coated finish for sheet steel housings.

        - Obsidian Black (Standard Color).

        - Battleship Gray.

        - Pearl White.

        - Titanium Silver.

        - Spartan Bronze.

        - Stainless Steel

        - Custom color as selected by the Architect.

    - Environmental Air Curtains: Models for Heights to 8 feet (2434 mm).

      - Discharge Nozzle:  Wedge-shaped discharge outlet nozzle with adjustable air foil vanes with a plus/minus 40 degree sweep front to back.

      - Air Velocity at Nozzle:

** NOTE TO SPECIFIER ** Select one of the following paragraphs for the model required and delete the ones not required. If more than one type is required show the location of each type on the Drawings or on the Schedule at the end of this Section.

        - LPV225-1: 25 Inch (635 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPV236-1: 36 Inch (915 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPV242-1: 42 Inch (1067 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPV248-1: 48 Inch (1220 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPV260-1: 60 Inch (1524 mm) Wide Units: 1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPV272-1: 72 Inch (1830 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPV284-2: 84 Inch (2133 mm) Wide Units:  1800 feet/min (9.1 m/s)   two 1/6HP motor/fan assembly.

        - LPV296-2: 96 Inch (2440 mm) Wide Units:  1800 feet/min (9.1 m/s)   two 1/6HP motor/fan assembly.

        - LPV2108-2: 108 Inch (2743 mm) Wide Units:  1800 feet/min (9.1 m/s)  two 1/6HP motor/fan assembly.

        - LPV2120-2: 120 Inch (3050 mm) Wide Units:  1800 feet/min (9.1 m/s)  two 1/6HP motor/fan assembly.

        - LPV2144-2: 144 Inch (3660 mm) Wide Units:  1800 feet/min (9.1 m/s)  two 1/6HP motor/fan assembly.

      - Air Speed at Floor: Minimum of 300 fpm (1.53 m/s) at 3 feet (914 mm) from the floor.

      - Air Inlet Grille and Filters:

        - Location: Front.

** NOTE TO SPECIFIER ** Select one of the following air inlet type paragraphs and delete the ones not required.

        - Type: Fixed air inlet grille.

** NOTE TO SPECIFIER ** Include the following optional filter paragraph if required and delete if not required.

          - Filter: Aluminum mesh, 1/4 inch (6.4 mm), washable.

        - Type: Filter Only as follows:

** NOTE TO SPECIFIER ** Include one of the following optional filter paragraphs as required and delete those not required.

          - Filter: Aluminum mesh, 1/4 inch (6.4 mm), washable.

        - Speed: 625 cu ft/min (295 L/s), minimum, per motor/fan assembly.

      - Sound Pressure Level At 10 feet (3 m) From Nozzle:

** NOTE TO SPECIFIER ** Select one of the following paragraphs and delete the ones not required. Coordinate selection with the Model specified above.

        - Single Motor/Fan Units (LPV2 25-LPV2 36):  49 dBA.

        - Single Motor/Fan Units (LPV2 42):  50 dBA.

        - Single Motor/Fan Units (LPV2 48):  52 dBA.

        - Single Motor/Fan Units (LPV2 60-LPV2 72):  53 dBA.

        - Two Motor/Fan Units (LPV2 84-LPV2 96):  53 dBA.

        - Two Motor/Fan Units (LPV2 108-LPV2 144):  54 dBA.

    - Insect Control Air Curtains: Models for Concession Stand Heights to 4 feet (1219 mm) or Customer Entry Heights to 7 feet (2134 mm) certified to NSF/ANSI Standard 37.

      - Discharge Nozzle:  Wedge-shaped discharge outlet nozzle with adjustable air foil vanes with a plus/minus 40 degree sweep front to back.

      - Air Velocity at Nozzle:

** NOTE TO SPECIFIER ** Select one of the following paragraphs for the model required and delete the ones not required. If more than one type is required show the location of each type on the Drawings or on the Schedule at the end of this Section.

        - LPN225-1: 25 Inch (635 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPN236-1: 36 Inch (915 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPN242-1: 42 Inch (1065 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPN248-1: 48 Inch (1220 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPN260-1: 60 Inch (1524 mm) Wide Units: 1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPN272-1: 72 Inch (1830 mm) Wide Units:  1800 feet/min (9.1 m/s)  single 1/6HP motor/fan assembly.

        - LPN284-2: 84 Inch (2133 mm) Wide Units:  1800 feet/min (9.1 m/s)   two 1/6HP motor/fan assembly.

        - LPN296-2: 96 Inch (2440 mm) Wide Units:  1800 feet/min (9.1 m/s)   two 1/6HP motor/fan assembly.

        - LPN2108-2: 108 Inch (2743 mm) Wide Units:  1800 feet/min (9.1 m/s)  two 1/6HP motor/fan assembly.

        - LPN2120-2: 120 Inch (3050 mm) Wide Units:  1800 feet/min (9.1 m/s)  two 1/6HP motor/fan assembly.

        - LPN2144-2: 144 Inch (3660 mm) Wide Units:  1800 feet/min (9.1 m/s)  two 1/6HP motor/fan assembly.

      - Air Speed at Floor:

        - Concession stand windows require a minimum of 600 fpm (3.05 m/s) at 16 inches (406.4 mm) from countertop with Aluminum mesh, 1/4 inch (6.4 mm), washable.

        - Customer entry doors require a minimum of 600 fpm (3.05 m/s) at 3 feet (914 mm) from floor.

      - Air Inlet Grille and Filters:

        - Location: Front.

        - Speed: 625 cu ft/min (295 L/s), minimum, per motor/fan assembly.

** NOTE TO SPECIFIER ** Select one of the following two paragraphs and delete the one not required.

        - Type: Fixed air intake grille.

        - Type: Aluminum mesh, 1/4 inch (6.4 mm), washable filter.

      - Sound Pressure Level At 10 feet (3 m) From Nozzle:

** NOTE TO SPECIFIER ** Select one of the following paragraphs and delete the ones not required. Coordinate selection with the Model specified above.

        - Single Motor/Fan Units (LPV2 25 to LPV2 36):  49 dBA.

        - Single Motor/Fan Units (LPV2 42):  50 dBA.

        - Single Motor/Fan Units (LPV2 48):  52 dBA.

        - Single Motor/Fan Units (LPV2 60 and LPV2 72):  53 dBA.

        - Two Motor/Fan Units (LPV2 84 and LPV2 96):  53 dBA.

        - Two Motor/Fan Units (LPV2 108 to LPV2 144):  54 dBA.

** NOTE TO SPECIFIER **  Select the optional components required from the following paragraphs for the air curtains specified. If more than one type of air curtain or component is required, indicate the location of each curtain and the components required for each location on the Drawings or on the Schedule at the end of this Section. Contact Mars Air Systems for specialty steam and hot water heaters other than those included in the specification.

  - COMPONENTS

    - Electric Heaters:  Provide complete with motor control panel factory mounted to air curtain housing, and thermostat to be field installed.

      - Temperature limit controller.

** NOTE TO SPECIFIER **  Thermostat is standard. Coordinate selection with Model specified above. Delete if not required.

      - Thermostat:  Wall-mounted, 208-Volt operation, with heater on/off selection.

      - Thermostat:  Wall-mounted, 230-Volt operation, with heater on/off selection.

      - Heating Coils: ETL approved as part of unit. CEC tested by ETL.  Factory mounted on the discharge end of the motor fan assembly and located within the nozzle outlet.

    - Steam Heaters:  Provide finned tube steam coils for field mounting on air intake side of the air curtain cabinet with opposite end connections.

      - Output:  Air curtain manufacturer's standard, one-row coils.

      - Coils: Certified in accordance with ARI 410.

** NOTE TO SPECIFIER **  Delete one of the following two connections paragraphs.

      - Connections: Same end, right hand, horizontal.

      - Connections: Same end, left hand, horizontal.

      - Casing:  One piece unpainted galvanized steel, bolted to air curtain housing.

      - Supply and return fittings on ends of casing.

** NOTE TO SPECIFIER **  Thermostat is standard. Coordinate selection with Model specified above. Delete if not required.

      - Thermostat:  Wall-mounted 115-Volt operation, with heater on/off selection.

      - Thermostat:  Wall-mounted 208-Volt operation, with heater on/off selection.

      - Thermostat:  Wall-mounted 230-Volt operation, with heater on/off selection.

      - Thermostat:  Wall-mounted optional 24-Volt operation, with heater on/off selection

    - Hot Water Heaters:  Provide finned tube water coils for field mounting on air intake side of the air curtain cabinet with opposite end connections.

      - Output:  Air curtain manufacturer's standard, one-row coils.

      - Coils: Certified in accordance with ARI 410.

** NOTE TO SPECIFIER **  Delete one of the following two connections paragraphs.

      - Connections: Same end, right hand, horizontal.

      - Connections: Same end, left hand, horizontal.

      - Casing:  One piece unpainted galvanized steel, bolted to air curtain housing.

      - Supply and return fittings on ends of casing.

** NOTE TO SPECIFIER **  Thermostat is standard. Coordinate selection with Model specified above. Delete if not required.

      - Thermostat:  Wall-mounted 115-Volt operation, with heater on/off selection.

      - Thermostat:  Wall-mounted 208-Volt operation, with heater on/off selection.

      - Thermostat:  Wall-mounted 230-Volt operation, with heater on/off selection.

      - Thermostat:  Wall-mounted optional 24-Volt operation, with heater on/off selection.

    - Door-Activated Limit switch(s):  Provide, field installed 250-Volts, 20 amps limit switch to control air curtain(s) as follows; Automatic on/off control, activates air curtain when door is opened and turns off when door is closed. Provide limit switch for direct control one 1 HP or up to two 1/2 HP single phase motors without a separate control panel. Provide a separate control panel for three phase motors controlled by a limit switch.

      - Type: Combination plunger/roller switch for swing and sliding doors.

** NOTE TO SPECIFIER **  Delete three of the following four paragraphs to suit enclosures for incidental contact, protection against weather and corrosive exposure and explosion proof as required.

        - Provide limit switches with NEMA 1 (20 amps) ratings in locations indicated.

        - Provide limit switches with NEMA 4X (10 amps) ratings in locations indicated.

        - Provide limit switches with NEMA 7 (10 amps) ratings in locations indicated.

      - Type: Magnetic reed switch and actuator for swing and sliding doors.  Industrial floor mounted or surface mounted switches for roll up doors.

** NOTE TO SPECIFIER ** Edit the following two paragraphs to suit the units specified. Delete the paragraph not applicable if it is not required.

      - Operation for Unheated Units:  Automatic on/off control, on when door is opened, off when door is closed.

      - Operation for Heated Units:  Automatic on when door is opened, off after time delay period after door is closed, maintaining heat in the event door is opened within delay time period. Field adjustable from 1 to 17 minutes.

    - Provide mounting hardware as required for the opening.

- EXECUTION

  - EXAMINATION

    - Verify that required utilities are in correct location and are of correct capacities for specified products.

    - Verify openings to receive air curtains are plumb, level, square, accurately aligned, correctly located, and in tolerance.

    - Examine surfaces to receive air curtains. If surface preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

  - INSTALLATION

** NOTE TO SPECIFIER ** Indicate the mounting location(s) on the Drawing or on the Schedule at the end of this Section. Units are typically wall mounted horizontally above the door opening.  Units can also be suspension mounted from the ceiling or vertically mounted along side the opening.  Units are ETL Listed (US and Canada) for either an inside or outside mount.  Heated units must be mounted on the inside or protected side of the opening. All ETL Sanitation Certified Series should be mounted at the Flying Insect Control heights referenced under the Insect Control Air Curtain products specified above.  The appliance is not to be used by persons (including children) with reduced physical, sensory or mental capabilities, or lack of experience and knowledge, unless they have been given supervision or instruction. Children are not to play with the appliance.

    - Install air curtains in accordance with approved shop drawings and manufacturer's printed installation instructions.

    - Install air curtains plumb, level, square, true to line, and weathertight, without warp or rack.

    - Anchor air curtains securely in place to supports.

    - Install sheet metal flashing as specified in Section 07620.

    - Install joint sealants as specified in Section 07920.

    - Install electrical power as specified in Section 16100.

    - Install door limit switches and adjust for correct operation.

    - Provide connection to piped services and utilities as specified in Sections of Divisions 15.

  - FIELD QUALITY CONTROL

    - Adjust air curtains to function properly.

    - Adjust air foil vanes located within the discharge nozzle as required for prevailing conditions at each opening.

    - Check heated air curtain performance on a calm day by measuring air temperature 6 inches off the floor. Optimal reading is halfway between the temperature inside and outside the building.

  - CLEANING

    - Clean air curtains promptly after installation in accordance with manufacturer's instructions.

    - Repair minor damages to finish in accordance with manufacturer's instructions and as approved by Architect.

    - Remove and replace damaged components that cannot be successfully repaired as determined by Architect.

  - PROTECTION

    - Protect materials and finish from damage until substantial completion.

** NOTE TO SPECIFIER ** For facilities with multiple types and sizes of air curtains use an Air Curtain Schedule to list requirements for each size, type, HP and power requirements of air curtain(s) required. Delete if not required.

  - SCHEDULE

    - Refer to Air Curtain Schedule appended to this section.

END OF SECTION